hiSOLAR INSTALLATION  SYSTEMS

The solar system module unit is designed to equip the trainee with knowledge, skills and altitudes necessary to understand and install solar installation system

Trainees will appreciate prior knowledge and skills acquired in Diploma/ craft certificate in Electrical Installation I.

OBJECTIVES BY THE END OF THE MODULE

- Understand the basic principles of solar system

- Create awareness in the application of solar systems

- Define relevant skills for installation of solar system

- Observe safety rules and standards when installing solar system

- Interpret solar system data and to determine solar sizes

- Institute quality control measures while installing solar systems

COURSE OUTLINE

| 1 | SOLAR INSTALLATION SYSTEM | -Solar energy and its conversion -Terms used with solar system -Methods of solar energy harvesting -Applications |
| --- | --- | --- |
| 2 | SOLAR PHOTOVOLTAIC SYSTEM | -Parts of photovoltaic -Functions of each part of a voltaic system -Layout of photovoltaic system |
| 3 | SOLAR SYSTEM ACCESSORIES | -Types of accessories -Types of cable joints -Wiring systems -Choice of wiring system -Tests performed on complete installations -Regulations governing solar installations |
| 4. | MAINTENANCE AND SERVICING OF SOLAR SYSTEMS | -Procedure for maintenance -repair and trouble shooting |
| 5 | SOLAR SYSTEM SIZING | -Terminologies -Sizing a solar system -Daily load energy demand -Equipment, cables and accessories sizing -Application of solar data |

Topic 1

SOLAR SYSTEM

- Solar - This is energy from the sun

Solar energy can be directly transformed I three useful forms. i.e chemical, heat or electrical SOLAR ENERGY

- energy.

SOLAR ENERGY CONVERSIONS

- Solar energy to chemical energy

- Green plants transform solar energy into chemical by the process of photosynthesis in order to make their food.

- Solar energy to heat energy (solar thermal)

- Solar heating devices (parabolic) dish, flat plate collector, mirrors etc., converts solar energy which can be used for cooking, water heating, drying etc.

- Solar energy to electrical energy

- Solar electric devices (solar cells) converts energy from the sun into electrical energy which is used in lighting, phone charging and running machines.

SOLAR RADIATION PRINCIPLES

- Solar Sunshine reaches the earth as a type of energy called radiation.

- Radiation is a process in which  heat is transmitted through vacuum / free space.

- Radiation is the high energy particle emitted from a given source.

- Solar radiation falls into different categories

- Infrared            - we feel it

- Visible light	 - enables us to see

- UV radiation	 - very high energy

DIRECT AND DIFFUSE RADIATION

- Direct radiation-A type of radiation that comes in straight beam from the sun and can be focused with a lens or mirrors.

- Diffuse radiation - A type of radiation is affected by the atmosphere, scattered by clouds, dust and absorbed by smoke.

Solar irradiance

- -Is the intensity of solar radiation within an area of 1m2.

- N/B  Intensity of the solar energy in kw/m2

- i.e Is the power received per unit area from the sun. It is measured in watts per square meter (W/m2). If a solar module / panel is facing the sun directly/perpendicularly the irradiants will be higher than if the module is at an angle with the sun.

- The angle at which the sun beam strikes the surface of the panel is called solar incident angle. More energy is received when the solar incident angle is 900.

- Tracking – Is the process of turning a solar panel to face the sun through out the day.

- NB. Irradiance starts to increase from dawn and reaches to its maximum at noon. Then it reduces until dusk.

- Its SI unit is kWh/m2

- Insolation/irradiation

- It is the total amount of solar energy received on a specified area over a specified period of time. It is measured in Wh/m2/day

PEAK SUN HOURS

- Represents the average amount of sun available throught the year. As peak sun of 1000w/m2 of power reaches of earth.

1000Wh per m2 = 1Kwh/m2 represents the solar energy recorded in one hour on group square meter surface directed towards the sun.

- Peak sun hours is also referred to as the equivalent time in hours, that a module would generate power as if under an irradiance of Standard test condition(STC) I.E 1Kw/m2

METHODS OF HARVESTING ENERGY

Solar energy can be harvested in two forms

- Heat /thermal solar

- Electricity

HEAT / THERMAL SOLAR

- Parabolic dish

It is a bowl shaped mirror that radiant energy is concentrated and utilized.

+

- Parabolic trough

- This focuses solar radiation along a pipe which runs through the centre.

- It contains mirror or reflective surface  of silver  or made from polished  aluminium.

- Single reflectors

- These are flat surfaces e.g mirrors, cigarette foils or aluminium foil which are arraged around a device to increase the radiation up on it.

- Flat plate collectors

- It  a metal box with glass or plastic cover on top and dark  colored absorber plate on the bottom,

- The sides and bottom of the collector are usually insulated to minimize heat loss.

- These are larger boxes with glass window in front an air spaces and black metal absorber plates with layer of insulation behind. Water heating collectors transfer heat from the absorber plate to the water through the pipe.

The main feature of flat plate collector are:

- Transparent glass – Allows heat from the sun to get into absorber plate

- Insulated sides	      - To prevent heat loss

- Absorber plate      - its painted black to absorb a lot of radiant heat

- High coiled pipes  - increase surface area of heat absorption

APPLICATION OF SOLAR THERMAL ENERGY

- Crop drying

Heat energy from the sun is used to dry crops and remove moisture and to facilitate storage.

- Water heating

Parabolic reflectors and parabolic collectors can be used to collect energy from the sun and convert it into heat energy which is used in heating water.

- Solar cooking

Parabolic dishes and box type cookers are used to harvest solar energy and use it for cooking.

Uses of solar  energy

Solar electric power can be applied in the following areas

- Household lighting

- Use to power radio, computers etc

- Phone charging

- Lantern charging

- Used in telecommunication. Most telecommunication systems are often installed in isolated area with no access to power. They are standalone power.

- Water pumping. Solar cell modules connected to electric pumps are used to pump water from rivers and boreholes.

- Electric fencing. Used in electric fence to scare away wild animals in game parks.

- Street lighting

- Security systems

ADVANTAGES OF SOLAR ELETRIC POWER

- Produce electricity quietly, without giving smoke or pollutants

- Require very little maintenance as compared to others e.g. generators since solar panel do not have moving parts

- Properly installed solar electric system are safe. Risk of electric shock is small because of the low system voltage. Fire risks are also lower as compared to the households which use kerosene.

- Solar electric system consume no fuel/funds since it uses freely available sun hence economical / cheap.

- Solar electric systems can be tailored to meet the power demand of each individual applications i.e. they can be expanded easily by adding more panels and batteries.

DISADVANTAGES OF SOLAR ELECTRIC POWER

- Appliances and lamps which run on low voltage are not readily available as compared to those of mains in the market.

- The initial cost of solar electric system is high by rural standards i.e. its very difficult for most people to raise the cash to buy system all at ounce

- Solar electric system require batteries for energy storage and these batteries must be carefully maintained.

- There is a lack of trained technicians to design and install solar electric system.

Topic 2

SOLAR PHOTOVOLTAIC SYSTEM

Parts of photovoltaic

- The four primary components for producing electricity using solar power which provides 240V AC power are.

- Solar panel (Photovoltaic module)

- Solar Battery

- Charge controller

- Inverters

- Loads

- Cables

BASICS OF SOLAR CELLS

SOLAR CELLS/PV CELL

- It’s a semiconductor device that converts the energy from sunlight into electrical energy through a process of photovoltaic effect

- photovoltaic effect-it is a process in which two dissimilar materials in close contact produce  voltage and current in a material exposed to sunlight.

- Solar cells are usually made from silicon or germanium, a semiconductor used the same material for transistor and integrated circuits.

- Free electrons cross the junction btw  two dissimilar more easily in one direction than in the one direction than in one another giving one side of the junction  a negative  charge  and the other positive side.

- An N-type semiconductor has electrons as the majority charge carriers (group v elements)

- An P-type semiconductor has holes as the majority charge carriers  (group iii elements)

- Its symbols is given by

- A solar cell is made up of a semiconductor material.

A semiconductor is that whose conductivity lies between conductors and insulators. E.g silicon and germanium.

- Underneath this sheet is a thicker layer of P-type silicon. When these two materials are placed together in contact, it creates P-N junction.

OPERATION

- When sunlight hits the PV cell, some of the electrons in the N-type silicon layer would be stimulated to move across the PN junction to the P type side of silicon layer, leaving the P type layer to have a higher voltage potential than the N-type.

- This creates an electric current flow when the PV cell is connected to the load. The voltage potential of a single PV cell is about 0.5V to 0.6 V at ( Voc)

c

- SOLAR PANEL (PV module)

- It is used convert sunlight into electricity and then charges the battery.

- The PV module consists of solar cells which converts the solar radiation energy to DC electricity.

- The solar cell is made from a silicon semiconductor.

- The output voltage of one solar cell is less than 1V which is not enough to drive any appliance.

- Therefore, several solar cells need to be connected in series to provide enough voltage. This is called a solar panel or a solar PV module.

- Several solar panels or a solar PV module  is called  array

Solar panels can be classified  in the form they are manufactured

1.Crystalline silicon PV module

2. Amorphous

TYPES OF SOLAR PANEL

- Is a widely used for solar PV modules. TWO  types of crystalline cells/solar cells are

a)Monocrystalline Silicon

- The monocrystalline silicon solar cell is made of a large single crystal of pure silicon.

- It consists of melting high-purity, semiconductor-grade silicon

- During this melting process, dopant impurity atoms such as boron (for p-type semiconductor) or phosphorus (for n-type semiconductor) are added to the molten silicon to dope the silicon; for PV-cells the preferred dopant is boron. (group 5)

- second step consists to dip a rod-mounted seed crystal into the molten silicon.

- The seed crystal has a well-defined crystal orientation.

- Next, the crystal's rod is carefully pulled out and rotated simultaneously.

- The appearance of the mono-Si is mostly black.

Fig 2: Monocrystalline silicon module

Properties of monocrystalline

- They are most expensive

- It has a higher efficiency than polycrystalline cell. That is they are more efficient in terms of energy generation

- they have a single-color tone

- they have a long life, up to 20years meaning that they are chemically    stable

- It has a smaller dimension compared to polycrystalline

b).    Polycrystalline

- Refers to cells made from many crystals.

- They are made in the same way as in monocrystalline cells.

- Solar cells based on poly-Si are very similar to monocrystalline modules.

- The same theory applies; the main difference is the fabrication process. Poly-Si cells are fabricated from pure molten Si in a square-like tank; the cooling down is an essential step because it determines the grain size and the distribution of impurities. The obtained ingots are cut in bars with a cross-section of 15.6cm x 15.6cm;

- finally they are sawn to get thin wafers. This fabrication process gives life to a multi-grain crystal structure.

- Compared to monocrystalline Si, the structure is less ideal resulting in a loss of efficiency (of about 1% compared to mono-Si) [3], but this drawback is overcome by lower wafer costs.

- A second advantage is the arrangement of the cell modules which are typically rectangular, rather than “pseudo-square” compared to mono-Si, so they can be packed very closely in the modules.

- The appearance of the poly-Si is distinctly blue (see figure 3) due to the missing absorption of higher energy photons.

- In fact, these high energy photons from the upper part of the visible spectrum are backreflected.

CHARACTERISTICS/DESCRIPTIONS

- Cheaper to buy  than monocrystalline

- Its slightly less efficient (9-13%) than monocrystalline.

- Have a long life

- Have multiple colour patterns

- Amorphous

Are made by depositing a thin film of silicon on to a sheet of another material such as a steel.

The panel is formed as one piece and individual cells are not visible as in other types. They are often seen in small solar cells such as calculator, watches,toys etc.

CHARACTERISTICS/DESCRIPTION OF ARMORPHOUS

- They are cheaper than monocrystalline and polycrystalline

- Have the lowest efficiency(3-6%) than poly and mono crystallines

- They are the most suitable for applications of 40W and below.

- The output of the solar panel is statre made ed in Watts,and the value is determined by multiplying the rated current and the voltage.

POWER in Watts = volts * Amperes

Example

- A solar panel is rated 12V 60W, Determine the current it can supply

Sln.

Watts = volts × Amperes

60 = 12 × A

A= 5A

FACTORS THAT DETERMINE THE OUTPUT OF A SOLAR PANEL

- Amount of solar radiation

- A lot of power is obtained when there is a lot of sunlight.

- The angle of the module with respect to the solar(sun)

- Much energy is collected when the solar pane faces the sun at an angle of 00.

- Temperature

- The temperature of the panel affects the output voltage inversely.

- For this reason, installers are encouraged to mount solar panels on poles, on structures above the roof, or in places where they are cooled by the wind in order to keep the output as high as possible.

- The major solar PV module that is affected by temperature is voltage. When the module temperature increases, the voltage decreases and the current slightly decreases.

- Shading

- A shadow or a shade across a module can almost stop electricity production by as much as 80%.

- Surface area of the panel

- The larger the surface area the higher the output.

MODULE WIRING / CONNECTION

- Solar panels can be wired in series, parallel or series-parallel in order to achieve the desired voltage and current.

SERIES CONNECTION

- Solar panels are said to be connected in series when the positive terminal of one panel is connected to the negative terminal of the other and so on.

- The result is that the voltage of the panels added together but the currents stays the same as that of one panel.

EXAMPLE,

Three  12V/3.5A panels are wired in series

Total voltage = 12×3  = 36V

Currents remains 3.5A

If one panel in series fails, it provides so much resistance that the other modules may not be able to operate.

- If one panel is shaded or faulty the current produced by unshaded panel flow through  a by- pass diode to avoid high resistance of the shaded panel.

- By-pass diodes-by pass current i.e providing alternative path for current and thereby maintain the continuity of power..

- By-pass diodes will not be use unless the panel are connected in series.

- The By-pass diode allows the currents from the other panels to flow through the the right direction.

- Shading can be caused by tree branch,debris ,snow or dust.

- By-pass diodes. – They ensures continuous flow of currents even if the panel is faulty.

- blocking diode – It prevents reverse flow of electric current especially at night or when the panel is not charging the battery.

PARALLEL

- It refers to connecting positive terminal of one panel to the positive terminal of the other panel, also negative terminals are connected the negative terminal of the other panel.

- The result is that the voltage remains the same but the current is the sum number of panels rating.

EXAMPLE,

if they are connected in parallel then

The voltage = 12V

Current = 10.5A

I-V CHARACTERITICS OF PV MODULE

- PV modules have different characteristics of its  power output profile

- This profile is shown by I-V curve

- Short circuit current(Isc)-maximum current obtained at 0 v

- Open circuit  voltage (voc)-maximum voltage obtained at 0A.

- Up to around 15 v delivered current is almost constant and drops quickly  at higher voltage. Output power is obtained by multiplying current by  voltage  Maximum power point(pm)- is obtained.

- This value(pm) is used to indicate output power of PV module called watt peak (WP)

- Current and voltage at maximum power  is called IMP and VMP respectively.

SOLAR BATTERIES

- It’s a device that converts chemical energy contained in the active materials directly into electrical energy.

- It is used to store d.c power or charge to used at night or during cloudy days

- Are designed to be charged and discharged.

TERMS USED IN BATTERIES

- Battery capacity

- The quantity or the amount of energy a battery can hold in a given time. The product of current in Amperes and time in hours

Battery Capacity= current (A) ×   Time (h)

=Ah

EXAMPLE

A lead acid battery maintains a constant current of 1.5A for 20 hrs before its fully discharged.

Battery capacity   = current   ×   time

= 20   ×   1.5

= 30Ah.

FACTORS AFFECTING BATTERY CAPACITY

- Temperature – Batteries are made to operate at a temperature of 150C – 400C. The lower the temperature the lower the capacity.

- Aging – Reduces the battery capacity. The older the battery gets the lower the energy it can hold.

- Area of plates – Battery capacity increase with plate area.

- Hour rate – This is batteries rate of charge or discharge. It sets the maximum rate at which the battery can be charged or discharged. Low hour rate is health to a battery but higher rate is dangerous.

- Specific gravity (density of sulphuric acid) – Battery capacity increase with specific gravity.

TYPES OF BATTERIES

- Batteries are classified either as:-

- Flooded batteries

- Sealed batteries

- Flooded batteries have topping facilities while sealed batteries are sealed at the factory and have no topping facilities.

1. FLOODED BATTERIES

- They are generally lead acid batteries. The various types in this case are

- Car or automotive Batteries

- Automotive batteries are also SLI batteries where the initials standards are for the function of battery i.e. Start, Lighting and Ignition.

PROPERTIES OF IGNITION batteries

- They are shallow cycled i.e. Large amount of charge can be drawn on a short period of time. Because of thin plates they are easily damaged when used for a short time only when starting a car engine and idle.

- Used for a short time only when starting a car engine and are under float charged i.e. permanently connected to a controlled charging system keep it in a charged state ready for use always.

- Low cycle life, less than 1000cycles i.e. 2 – 3 years.

- Low self-discharged i.e. means charge lost from batteries left standing uncharged. This occurs because of chemical reaction within the cells.

- It is not suitable for solar electric system.

- Traction batteries

- These are batteries used in battery electric vehicles and tracks e.g. Folk lifts used for lifting luggage in warehouses and stores.

PROPERTIES OF TRACTION BATTERIES

- Deep cycled – i.e. can tolerate deep discharge unlike automotive batteries

- Very good cycle life, about 1500 cycles that around about 3 – 5 years

- Have high self-discharge about 7% in a month

- Good for solar use.

- Stand-by batteries

-Are used for power emergency supplies in industries and telecommunication. They are used for stand-by power in case of power or engine failure.

PROPERTIES OF STAND-BY BATTERIES

- Low water loss

- Kept on float charge

- Has to stay in charged state for it to work

- Stays on full state of charge

- Moderate cycle life (5 – 10 yrs.)

- Low self-discharge

- Not suitable for solar use

- Not designed for deep discharge

- Solar batteries

Are specially made to store energy from module arrays. Locally the ABM solar system (associated battery manufacture is a modified battery manufacturer.

PROPERTIES OF SOLAR BATTERY

- Very low water loss (topped up annually)

- Battery cycle life (3000 – 1000 cycles i.e. 5 – 10 yrs.)

- Low discharge rate (2 – 4% per month)

- Thick lead antimony plates with maximum amount of active materials in space and heavy connectors and large electrolyte reservoir.

BP solar company are the major exporters of such cells which are of high quality solar life and more expensive.

2.SEALED BATTERIES

They have no provision of topping up. Examples are:

- Nickel cadmium batteries

Are commonly used in electric showers, electronic photoflash equipment’s telephone systems, mobile phones

- Captive Electrolyte (gel) Batteries

Are used in a non-liquid electrolyte to eliminate the problems of water through gassing. They are also used in solar lanterns.

- Nickeled cells

Are nickeled cadmium cells.

They are made in small sizes AA or size D and look exactly as normal cells.

They have a voltage of 1.5V but are chargeable.

They can be used to power small radios, calculators and wall clocks.

CHEMISTRY OF LEAD ACID CELLS

The fundamental part / active parts are positive parts;

- Positive active material – lead peroxide (PbO2) dark brown chocolate

- Negative active ma terial – spongy lead (Pb) slay Grey

- Electrolyte		  -   Dilute sulphuric acid H2SO4

Electrolyte – This is a conducting medium in which the following electro current takes place by migration of ions(± or –ve ) charges) e.g H2SO4.

PbO2+Pb+H2SO4                                                                        PbSO4 +H2O

Discharging

Charging

DISCHARGING

- When the cell is fully charged its positive plate or anode is PbO2 ( dark brown chocolate) and negative plate or cathode is Pb ( slay Grey)

- When cell discharges H2SO4 dissociates  to form H2 in the positive and  SO4 ions  in the cathode.

- At the anode  hydrogen H2 combines with oxygen of PbO2   and H2SO4 lead to  PbSO4

At the cathode Pb ,  SO4 combines  with it to form  PbSO4

During  discharging

- Anode and cathode becomes somehow withish in colour

- Specific gravity of acid decreases

- Terminal cell voltage decreases

DURING CHARGING

When the cell is recharged the H2 ions move to the cathode and SO4 moves to the anode.The following reaction takes place

Cathode    PbSO4+H2                                   Pb+H2SO4

Anode  PbSO4 +H2O                    PbO2+Pb+H2SO4

During charging

- positive plate or anode is PbO2 ( dark brown chocolate) and negative plate or cathode is Pb ( slay Grey)

- Terminal voltage increases

- Specific gravity increases

SELF DISCHARGE OF LEAD ACID CELLS

- If left standing all batteries lose charge slowly by a process called self-discharge. This is because of the reactions within the cells.

To avoid self-discharge

- Store the battery off the floor to avoid self-discharge

- Keep the top surface of the battery clean

- Keep the terminals greased. If the battery is left in a discharged state for a long period of time it will be damaged because of sulphation.

MAINTENANCE OF BATTERIES

1.Cleaning the top of the battery

- This avoids high rate of self-discharge caused by electrical conduction through acid accumulating on top of the battery.

- Cleaning terminals and contacts ensures good electrical contact with solar module and acid.

- Application of grease /petroleum jelly to the terminals prevent them from becoming corroded.

2.Regular checking of state of charge

- to ensure the battery is performing well. It may also      help to detect a bad cell or when the battery is old

3.Checking the electrolyte level in each cell.

- If the level has dropped, top with distilled water.

- Do not add tap water since it contains impurities. Rain water or de-ionized water can be used.

NB. Never add acid.

- Why? Because the acid component does not evaporate. If more acid is added its concentration increases and it reduces its efficiency of the chemical reaction. Also do not add too much distilled water because the electrolyte level must be below the maximum level indicated in the battery.

4.Giving the battery occasional equalizing charges to mix up the electrolyte.

- Equalizing charges are charges well above the normal charges which cause the electrolyte in the battery to bubble and got mixed up.

- This charges can be done preferably in a cloud season or when the solar radiation is low. This is done to avoid stratification.

- STRATIFICATION is define as accumulation of acid component at the surface and the water component at the top.

Stratification can also be reduced by shaking a battery.\

- The cells of lead acid battery should be ventilated

- to allow hydrogen and oxygen gases to escape during charging and provide opening for topping up.

Voltage per cell when battery is fully charged = 1.712V

For battery = 12.7V – 14.4v

When fully discharged Voltage per cell = 1.9v

BAD CELLS

- To check for a bad cell measure the state of charge of each cell using the hydrometer.

- If its not available you can still check a battery in slow state of charge by removing the caps of all the terminals and short them. *Short the terminal with an insulated wire.

- If a cell is bad, it bubble furiously and produce a discharging sound.

COMMON USES OF SOLAR ELECTRICITY

- Solar electricity is electric power generated from sunlight using devices such as solar panel, charge controller, battery and inverter.

HOW SOLAR ELECTRIC SYSTEM DIFFER FROM MAINS (ELECTRICAL POWER)

- Solar systems are based on low voltage DC, not 240V AC.

- Solar systems stores power in batteries

- Power is generated on site by photovoltaic equipment’s

- For solar system to be economical all energy produced must be used efficiently.

METHODS OF CHARGING BATTERIES

- Use of mains electricity

- Engine charging e.g. motor vehicle

- Solar charging – solar modules converts solar energy to electric current

- Charging with battery charger

- Charging with a bicycle alternator/dynamo

MEASURING BATTERY STATE OF CHARGE(S.O.S)

- The state of charge is a measure of energy remaining in the battery. It tells whether the battery is full fully charged, half or fully discharged.

- The cells of a fully-charged battery have a state of charge of 100%.

- There are two ways of measuring battery’s state of charge;

- A voltmeter

- Hydrometer

- VOLTMETER

It measures the voltage of the cells.

HOW TO USE A VOLTMETER TO MEASURE THE STATE OF CHARGE

- Disconnect the battery from the load and solar charge.

- Wait for at least 20 minutes to allow the cell voltage to stabilize.

- Before taking the measurements connect the voltmeter leads to the positive and negative terminal of the battery.

- Read the voltage readings on the voltmeter.

ii.    HYDROMETER

- It measures the density (specific gravity) of sulphuric acid in each cell. As the cell is discharged, the sulphuric acid is converted to water which lowers the density of the acid.

Steps to follow;

- Draw the sulphuric acid into the hydrometer from the battery cell while the nozzle is placed in the cell.

- The scale of the hydrometer floats at a level that varies according to the density of the acid, also according to the state of charge of cells.

- Take the reading of the density from the scale floating in the acid of the hydrometer.

- Consult a state of charge verifying specific gravity table determining the state of charge as shown below.

| STATE OF CHARGE | Voc | SPECIFIC GRAVITY (gms/ltr) |
| --- | --- | --- |
| 100 | 12.74 | 1230 |
| 80 | 12.50 | 1203 |
| 60 | 12.25 | 1175 |
| 40 | 12.00 | 1147 |
| 20 | 11.75 | 1120 |
| 0 | 11.51 | N/A |

- Cycle, cycle life and deposit discharger

- A battery is charged each day by the by the solar module and then discharged by load each night.

- Each charge period together with the following discharge period is called a cycle

- The rated life cycle of a battery is the number of cycles a battery is expected to last before its capacity drops to 80% of its original / rated capacity.

Depth of Discharge (DOD)

- It indicates the level of discharge of a battery in percentage (%).

- It tells how much batteries are discharged in a cycle before they are charged again. It specifies the percentage of the capacity drawn out.

Based on DOD, batteries are classified as shallow cycle batteries and deep cycle batteries

SHALLOW CYCLE BATTERIS

- They should not be discharged below 80% of state of charge on a regular battery basis. i.e It allows DOD of 25% without shortening its life.

DEEP CYCLE BATTERIES

- Is one which should not be discharged below 40% of state of charge? I.t It allows DOD of 50%.

DEEP DISCHARGE CYCLE

- Is a cycle in which the battery is completely discharged? This occurs during long cloudy period or when the load is much larger than the solar charge, this is dangerous.

- If the battery is very low after a week or more of cloudy weather, it should be immediately charged by an alternative method. I.e. the rate of life cycle is shortened by deep discharges.

- CHARGE CONTROLLER

- It protect batteries against overcharge and over-discharge. Note that it does not regulate voltage / current.

- They are sort of switching devices that have two switches, one between PV module terminal and battery terminal, the other is between load terminal and battery terminal.

- Since charge controller do not convert the form of energy,( there is no loss when energy is flowing through the charge controller).

- The switch on the PV module is used for overcharge protection, while the switch on the load side is used for over discharge protection.

- Charge controller are rated based on the amount amperage, they can process from a solar array.

NB

- If a controller is rated at 20 ampere it means that you up to 20 amperes of solar panel output current to this one controller.

- The most advanced charge controllers utilize a charging principle referred as pulse  width modulation (pwm) which ensure the most efficient electrical charges and extends the life of the battery.

- They also include maximum power point tracking (MPPT) which maximize the amount of current going into the battery from the solar array by lowering the panel output voltage which increases the charging amperes to the battery.

- Many charge controllers also offer low voltage disconnect (LVD) and battery temperature compensation (BTC) on optional feature.

- The LVD feature permits connecting loads to the LVD terminals which are then voltage drops too far, the loads are disconnected to prevent potential damage to both the battery and the loads.

- BTC (battery temperature compensation) adjusts the charge rate based on the temperature since batteries are sensitive temperature variations above and below 750 FB.

TYPES OF CHARGE CONTROLLERS

- Shunt type controllers

- Series type controllers

FUNCTIONS OF CHARGE CONTROLLER

Allows the user to monitor the system for potential system problems.

T protects the battery from overcharging – overcharging causes voltage level to go down which cause sulphation on the plate of battery.

Low Voltage Disconnect (LVD) – The LVD continually measures the state of charge of battery. If the battery voltage drops below a certain level, the charge controller automatically disconnects the battery. I.e. the battery has been disconnected ounce.

NB. Before buying the charging controller check the disconnect voltage. It should be between 11.1V to 12.9V.

OVERCHARGE PROTECTION

Charge controller has an overcharge protection feature that prevent the module from overcharging a battery.

*The controller may reduce the current from the module to trickle charging. (Trickle charging means – a low current charges so that the battery is not charged after it is full)

-The controller may charge OFF and ON over a period of time.

-Controllers may include other features to enhance the system performance e.g. ammeters, Voltmeters, and Amps hour meter (measures power output)

BLOCKING DIODES –This prevents backflow of current.

SURGE PROTECTORS – Protects the systems components and appliances against rapid power increase commonly during lightning strikes.

CHOOSING CHARGE CONTROLLERS

Charge controllers are rated according to the input current from the module. E.g. 5Amp unit will accept charge of 5A from the module. The smallest available units are rated at 2A which can

Handle 20W of power. It can power black and white TV’s, fire lamps and cassette players.

INVERTER

Is a device that converts DC power stored in a battery to a standard of 240V/ 120V AC. Most solar power system generate DC current. Nearly all lighting appliances, motors, electronics are designed to use AC power, so it takes an inverter to convert the DC to AC.

In the inverter, DC is switched back and forth to produce AC. Then its transformed, filtered stopped etc to get it to accepted wave form.

Inverters come in two basic outputs designs;

- Sine wave

- Modified sine wave

Most 120v AC devices can use the modified sine wave with some exceptions such as laser printers which use tracks or silicon controlled rectifiers which can be damaged when used on the modified sine wave power.

Motors and power supplies run warmer and lose efficiency a modified sine wave power.

Some appliances like fans, amplifiers and cheap fluorescent light gives out an audible buzz sound and modified sine wave.

Modified sine wave inverters make the conversion to AC very efficient. They are inexpensive and are used in most of electrical devices.

Sine wave inverters can virtually operate anything.

Compound internal features in inverters are;

- Internal battery charges – which can rapidly charge when an AC source such as generator or utility power is connected to the inverters input terminals.

- Auto-transfer switching feature; - it’s a feature which enables switching from either one AC source to another

- Battery temperature compensation

- Internal relays – control load, automatic remote generator starting stopping and many other programmable features.

TOPIC 3.

SOLAR SYSTEM ACCESSORIES

Types of accessories

- Wiring system AC and DC switches

- Socket outlets

- Lamp holders

- Ceiling roses

- Patresses

- Consumer control units

Choice of wiring system Choice of wiring system

- Sheathed wiring system

- Tough rubber sheath

- Polyvinyl chloride (PVC) sheath

- Polychloroprene (PCP)

Tests procedures for an installation

Types of cable joints

- Telegraphic joint

- T- joint married joint

- Bell hangers joint

- Straight twist

- Britannia joint

- Scarf joint

WIRING SYSTEM

- Wiring system is an assembly of parts used in the formation of one or more electric circuits.

- It consists of the conductor together with its insulation, its protection against mechanical damage (sheathing, armoring) and certain accessories for fixing a system.

- A cable is a length of a single conductor having one or more several wires stranded together. The wires are also called cores of a cable. A cable consists of a three essential parts.

- Conductor  - carrying currents

- Insulation - to provide the means to prevent leakage of currents.

- External overall protection (sheath) – protects against mechanical damage, chemical effect, fire or other external factors.

FACTORS TO CONSIDER WHEN CHOOSING A WIRING SYSTEM

Factors that are considered when choosing a wiring system

- Type of building/nature of building – whether the installation work is for a permanent building or for extension to an existing building or temporary building.

- Flexibility – whether the wiring system must be one which will allow it to be easily extended sometimes in future e.g offices.

- Installations condition – whether the installation is likely to be subjected to mechanical damage, moisture, fumes, weather, abnormal temperatures, explosive gas or vapour.

- Appearance/aesthetic – Whether the building is such that the electrical installation must be hidden or its appearance must be allowed for beauty.

- Durability – whether the installation is to last for time of building----------

- Cost – whether the amount of money is available for the wiring system.

- Safety – safety should be considered so as to minimize danger e.g a school where children play.

TYPES OF WIRING SYSTEM

- SHEATHED WIRING SYSTEM

- Tough rubber sheath

- PVC sheath

- PCP

- CONDUIT WIRING SYSTEMS

- SHEATHED WIRING SYSTEM

The wiring consists of an insulated conductor provided with a sheath that protects against mechanical damage. The insulating materials are impregnated paper,rubber,plastics and mineral insulation. The sheathing materials include; lead, tough rubber, plastics, aluminium and textiles.

- (TRS) Tough Rubber sheath or protected cables

They are commonly known as Trs ( tough rubber sheath). The insulation is vulcanized rubber and the sheath is tough rubber.

The insulation is vulcanized-rubber; the sheath is tough rubber

The cable is available in a single core (circular section) flat twin, three-core and twin with earth continuity conductor (ECC)

DIAGRAM

Advantages of TRS

- Cheap

- Flexible

- Easy to install

- Easy to withstand heat

Disadvantages of TRS

- Rubber is affected by oil

- Weakness of rubber to withstand severe mechanical damage

- They can be fixed with brass tuckle cups with steel pins

- PVC SHEATH (polyvinylchloride sheathed)

The conductors are insulated with PVC and the sheath is of PVC.

PVC is much less affected by oil as compared to rubber.The insulation resistance for pvc is much lower. The pvc system is available as single core(circular), flat twin, three core and twin with earth continuity conductor.

Advantages

- Less affected by oil

- The insulation resistance is much lower tann that of rubber

Disadvantages of PVC sheath

- It softens when warm unlike rubber which hardens and this factor precludes it from a number of installations applications

- Their accessories and methods of fixing PVC are much the same to those of TRS

- PCP( polychloroprene)

The cable consists of conductor insulated with vulcanized rubber and sheathed with PCP which is tough rubber like substance. This form of wiring is suitable for farm wiring where steam, ammonium fumes, lactic acid, milk fats, direct sunlight and heat can be experienced. It is installed in the same way as TRS or PVC.

- LAS (Lead-alloy sheathed)

The LAS system consists of conductors which are insulated with vulcanized rubber, taped, taped and sheathed with a lead alloy (lead with a small proportion of tin and antimony). The lead sheath can be used as an earth-continuity conductor.

It is available in single single-core (circular), twin-core, three core and twin with –ECC. Fixing is by buckle clip used for PVC and TRS system

ADVANTAGES

- Can be adopted for use with a conduit system

- Its very soft

DISADVANTAGES

- Because of its softness it can be damaged severely by blows from any hard objects

- LAS are liable to corrosion when they come in contact with damp situations

- PILC (paper insulated, lead-covered)

PILC are mainly used for external underground distribution system. It has a wide application for internal distribution in factories and other industrial premises. The paper is impregnated and must be protected against the ingress of moisture. Further protection against mechanical damage is provided ny armouring.

Fixing is by clips or saddles

- MIMS(Mineral isulated, metal sheath)

They consists of copper(or aluminium) conductors contained in a copper(or aluminium) sheath. The most common type is the MICS cable with copper as the main metalfor conductors and sheath.

ADVANTAGES

- They are self contained and require no futher protection (evn against high temperature anf fire)

- They are impervious to water and oil and immune from compensation

- Because the sheath and insulant are inorganic, the cable is virtually ageless.

- Installing is simple

- Current rating is higher than that of TRS,PVC or PILC cables

- Because the sheath is copper, it offers an excellent self-contained ECC.

Applications for the cable include industrial installations and hazardous areas

- CONDUIT WIRING SYSTEM

The material used for plastic conduits is PVC.

There are two types of conduits

- Flexible

- Rigid

The flexible type can be bend without tools while the rigid type is bent with a carefully application of a flame to soften it.

Fixing are by saddles.

RIGID TYPE

It is classed as either light gauge or heavy gauge.

For light gauge, -It has thin walls and is available as close-joint, brazed ir welded joint and solid drawn. It is not heavy enough to withstand threading and so presents  problem where earth continuity must be maintained. The conduit must be prepared before connecting by removing the enamel. The conduits are erected before cables are drawn in into them.

For heavy gauge or srewed conduit Its available as seamwelded, and solid drawn. Welded seam conduit is used for most good quality installation work. Because solid drawn conduit is more expensive than seam welded, its use is generally restricted to gas tight and explosion proof installation work.

COPPER CONDIUT

ADVANTAGE

- High resistance to corrosion

- Excellent ECC

- The system can be soldered

DISDVANTAGE

- The system is expensive

ALUMINIUM CONDUIT

ADVANTAGES

- Its light in weight

- Excellent ECC because its resistivity is a little higher than that of copper

- Easy to work with

- Can be suited to tropical conditions

DISADVANTAGE

- Can corrode where dissimilar metal is in vicinity

FLEXIBLE CONDIUT

Generally used for the final connections to machinery ( e.g. electric motors) where vibration and the possible need to adjust the position to an equipment makes a rigid conduit connection unsatisfactory. Also they can be used where there is a need for complicated bends and sets. Its used for short runs where mechanical damage is likely to occur

The flexible conduit consists of a spirally-wound, partially-interlocked light gauge galvanized steel strip, and may be water tight or non-water tight. It can be obtained with a PVC oversheath.

DISADVANTAGE

Since its not accepted as an ECC, a separate ECC must be run between the special brass adaptors used to join the flexible to the ordinary srewed conduit.

TYPES OF CABLE JOINTS

- Britannia joints –

This joint is used for single copper wires which have inconsiderable tension when in use. Each of the wires is thoroughly cleaned and lined for a distance of about 75mm. About 6mm of the end is bent over at right angles and forms a stop to prevent the joint from pulling out. The two wires are then brought together over a distance of 50mm with stops in the opposite.

Diagram

The binding is carried past each of the stos about 4 or 5 turns. The whole joint is soldered. No insulation is required.

- Scarf joint

Each of the two ends is carefully chamfered by filing over a distance

- Straight twist joint

- Tee Twist joint

- Tee- joint -on straded cables

- Telescope joint -for larger cables

- Married joint

- Pig trail joint

- Duplex joint

QUALITIES OF A GOOD CABLE JOINTS

1. Should be able to withstand the circuit current under normal condition and fault currents without failure.

2. Should maintain the conductivity and mechanical strength of the conductor on which the joint was made.

TESTS PERFORMED ON COMPLETED INSTALLATION

TYPES OF TESTS TO BE CARRIED OUT

- ELECTRICAL WIRING TESTS

- continuity and switching tests

Continuity and switching tests – They are carried out on the load side of individual circuit to check that the circuits are continuous when switched ON i.e. if cables are not broken or disconnected. That the switches are working well.

To perform these tests the cables are at right outlet points and sockets are short-circuited. All switches are turned OFF and the multi-meter is set to the buzzers function.

If the continuity and switching is good, the buzzers will sound when the switch is turned ON.  If it don’t the continuity is fault and need to be corrected.

- polarity Test

i.e for load circuits outlets outlets and connect lights. Before connecting the lights or using sockets, its important to ensure that all poles at all outlets is correct. Reverse polarity can cause permanent damage to the DC loads unlike the AC loads.

With multi-meter, connect the red and black leads red and black wires respectively to power outlets.

We should get a positive reading but a negative reading when reversed in a multi-meter.

- insulation resistance Test

This is to ensure cables are insulated and at no point the negative and positive cable should come into contact. I.e. no possibility of short circuit due to fault by cables.

To perform this test, turn on switches and ensure cables terminating lights at lights are open.

- Test for voltage drop

This is to done to check appropriate cable gauge is used.

- MODULE ARRAY TESTS

This is to check its performance as per the specifications. It is also to confirm the polarity conforms to the standard colour coding i.e red is +ve and black is –ve.

Measure the short circuit current as well as open circuit voltage.

Check battery voltage and polarity. This is done to ensure that the battery is discharged. Ensure that the polarity is correct before connecting to the charge controller.

REPLACING AND TROUBLESHOOTING

Trouble shooting – It involves identifying faults and carrying out simple repair

QUESTIONS TO ASK BEFORE TROUBLESHOOTING

- What was the weather condition before the problem?. If the weather was cloudy, its more likely that the load has taken more energy than the solar module produced.

- Is the system new? Does the owner know how to use and maintain.

- What is the type, condition and age of battery? If the battery is old this is the cause of the problem. If new, clean and well charged look for the problem elsewhere.

- Are all fuses and circuit braekers okey? Locate all the fuses, check if they are blown out.

- Are all the wires connected accurately, corroded, broken etc?

- What is the condition are modules in? are they dusty or shaded.

TROUBLESHOOTING GUIDE

| No. | PROBLEM CAUSE | HOW TO FIX IT |
| --- | --- | --- |
| 1 | There is no solar charge | Check and fix connections to the module |
| 2 | Battery acid(electrolyte) is low | Add distilled water to the cells |
| 3 | Bad connections to control terminal | Check for broken wires or loose connections |
| 4 | Defective battery / cell | Check for state of charge of each cell. If there is a significant difference between the cells, replace or repair them |
| 5 | Loose/corroded battery terminal | Clean and tighten battery terminals |
| 6 | Dusty module | Clean the module |
| 7 | Blown fuse | Replace |
| 8 | Over-use of a system | Leave appliances of lamps ‘OFF’ for one week to allow recharging or recharge battery by other means |
| 9 | Battery will not accept charge | Find out the age of the battery. If old replace. |
| 10 | Voltage drop between modules and battery too high | Check the voltage drop. Replace with a large modules. |
| 11 | Defective controller | Check operation of the controller. Repair or replace it. |
| 12 | Short circuit along the wires leading to the modules | Locate and repair the loose connections |
| 13 | Thick coating or soot or dust on module | Clean the module with water using a soft cloth |
| 14 | Blown module | Check for broken cell, broken glass or poor connection inside the module – Replace the solar module cell. |
| 15 | Bad tube, globe ballast inverter | Replace and buy a new one. |
| 16 | Bad connection in wire | Locate the broken or loose wire and repair |
| 17 | Tubes or globes having short life | Check voltage of the system. Too low or too high. |
| 18 | Bad connection in the wire | Locate broken or loose wire and repair |
| 19 | Switch is off | Turn switch on |
| 20 | Broken appliance | Try appliance where there is a good power supply. Repair or replace |
| 21 | Fuse was too small | Use a fuse 20% larger than the contained power |
| 22 | Lighting or power surge | Replace the fuse |

SIZING

Is a process of getting the correct combination of module, battery size, charge controller, inverter, cables and other accessories to give the necessary power or energy in an installation. It involves a number of steps:

- To calculate the total daily system

Its amount of energy required each day to power the load. It is measured in watts hours and amperes hour (Ah). In calculating the total daily energy requirements we use the worksheet below.

| Column A | Column B | Column C | Column D | Column E |
| --- | --- | --- | --- | --- |
| Lamp or appliance | Voltage (V) | Power in Watts | Daily use hour | Daily energy use (Wh) |
|  | BOX G |  |  | BOX F |

Column A       - list of all the lamps and appliances to be powered by the system

Column  B	-list all appliances and lamps voltage

Column C	-list all lamps and appliances power rating

Column D	-It has got a list of hours per day that each lamp/appliance will be used

Column E	-Multiple of the power of each load by the number of hours used per day.

BOX F		-Add all the values in column E and write the total in column F to get the

Daily energy demand in Watts’s hour (Wh)

NB. For battery capacity you measure ampere hour (Ah) i.e. total charge. Therefore the Wh can be converted to ampere hour (Ah) by dividing with Voltage (Total voltage in BOX G)

i.e. 	Watts   =   voltage (V)   ×   current (I)

Watts hour = voltage (V)× current (I)  ×  hours

So: Ah = Wh ÷ voltage

Then estimate the losses or efficiency of battery, c/c controller and inverters

Efficiency of battery			= 80%

Output Performance of PV module	=80%

Average insolation in Kenya		=5.6 kWhm2/day

NB. System voltage e.g. 12V for one battery

Daily system charge = battery capacity

WIRING AND FITTINGS

This topic deals with choosing cable size, type and fittings and methods of earthing the system for PV.

HOUSE WIRING

- Low voltage DC systems normally use cables of at least 2.5mm2 for sockets, 1.0mm2, 1.5 mm2 for lights without a separate earth wire which is also known as thin plate.

- In solar electric system multi-stranded wire should be used instead of single stranded wire.

- Those cable which can be exposed to the sun*

- Also when wires pass underground or up outside walls they should be run in conduits.

SWITCHES, SOCKETS AND FUSES

Switches are used to turn lamps ON and OFF. DC types of switches are preferred for low voltage solar electric system. Because they are not available in some areas, installers commonly use 240V switches. Standard lights switches are sized as 3A and 5A and can safely be used for lamps up to 36 to 60 Watts.

SOCKETS

Sockets are devices into which a plug is inserted, to access power to an appliance. A standard 240V AC sockets are commonly used in small solar electric. These sockets rated 13A and are capable of providing loads up to 150 Amperes.

NB. Low voltage system requires high current to carry high voltage system.

FUSES

Fuses are devices that are used to protect equipment’s and loads whenever there is high current due to short circuit. When a short occurs, the fuse blows and opens the circuit so that current will not flow.

MCB’s (miniature circuit Breakers) – Are small fuses which automatically breaks when there is a fault. They can be switched ON ounce the problem has been reconnected.

SIZING FUSES

Fuses are sized to blow OFF when the 20% greater than the maximum expected current flow in the circuit.

To calculate the size of fuse required the following steps are followed

- List the circuit to be protected .Determine the maximum power possible by adding the power in Watts of all the loads.

- Divide the power by system voltage.

- Increase this figure by 20%. This is the size of fuse required e.g If a 12V system circuit includes 15Watts TV and 3 8watt lamps. Calculate the fuse size required.

SOLUTION

MAX

POWER      =     15 +  3  ×  8  = 39

=   39W ÷ 12V  =  3.25A

120% × 3.25    =   3.9A

Hence 4A fuse is required.

EARTHING SYSTEM

Earth wires protect against electric shocks to people against damage to the system against lighting.*add*

Low voltage systems are earthed by connecting the black wire to earth. It is made by connecting –ve terminal of a battery to earth rod.

Solar modules are earthed by running heavy gauge e.g wires from the frame and –ve terminal of each module to an earthing rod driven into the ground.

Some of the 40hp or larger modules have a terminal for the attachment.

*CHOOSING THE CORRECT SIZE OF CABLES

Whats a voltage drop – this is loss of voltage due to resistance of long cables. The voltage drop affects the lamp. its good to allow a voltage drop of more than 5% on a cable*

Module is rated at 4hp n below*

No wire carries current greater than 4A.

Calculating voltage dropdetermines the size of wire to be used inorder to calculate voltage drop one must know three values:

- Current flow to the cable

- Distance of the cable

- The resistor factor (k) of the intended cable ohm per meter.

RESISTANCE FACTOR k FOR COPPER WIRE

| WIRE AREA MM2 |  |  | RESISTANCE FACTOR k ohm per meter |  |  |
| --- | --- | --- | --- | --- | --- |
| 1.0 |  |  | 0.04 |  |  |
| 1.5 |  |  | 0.027 |  |  |
| 2.5 |  |  | 0.016 |  |  |
| 4.0 |  |  | 0.010 |  |  |
| 6.0 |  |  | 0.0068 |  |  |
| 10.0 |  |  | 0.0040 |  |  |
| 16.0 |  |  | 0.0026 |  |  |
| Column A Cable run | Column B Distance | Column C Max current (A) |  | collumn D k in Ω/m | Column E Total R R × length |
| Battery -kitchen | 50m | 12A |  | 0.027 | 0.027×50=1.35 |
| Battery –sitting room | 7m | 2A |  | 0.016 | 0.16×7=0.71 |

TEST 1

Question one

- Define the term accessories  (2mks)

- List six accessories

- Name any five types of cable joints.  (5mks)

- Outline the procedure for making the following cable joints using diagrams

- T-joint

- Britannia joint

- Scarf joint

Question two

- State two advantages and two disadvantages of Tough rubber protected cables (T.r.s)   (2mks)

- Explain any three types of wiring system

- Explain five factors to be considered when choosing type of wiring

- What is troubleshooting

- List any three questions to ask before trouble shooting

- Using the troubleshooting guide, list any three problems causes. State how to fix each of them.

Question three

Define the terms

- sizing

- Daily load energy demand

- A farmer has the following appliances

| Appliance | Voltage | Power (w) | Daily use time | Daily energy use Wh |
| --- | --- | --- | --- | --- |
| Sitting room lamp | 12V | 13W | 3hrs |  |
| Kitchen lamp | 12V | 13W | 2hrs |  |
| Bed room 1 | 12V | 8W | 2hrs |  |
| Bedroom 2 | 12V | 8W | 1hr |  |
| Cassette player | 9V | 10W | 3hrs |  |
| 14’’ colour TV | 240 AC | 80W | 2hrs |  |

- Use the following efficiencies

Efficiency of DC-AC  inverter		= 90%

Efficiency of battery			= 80%

Out put Performance of Pv module	=80%

Average insolation in kenya		=5.6 kWhm2/day

- Calculate the total daily energy use in Wh

- Choose the system voltage

- Choose the appropriate PV panel for the farmer

Q 4. Explain any three types of tests to carried in a PV system inspection and testing.

Q5.

- Distinguish between parabolic dishes and parabolic troughs with methods of solar harvesting

- Describe flat plate collectors as ameans of solar harvesting

- List two advantages and the disadvantages of direct solar driers

Q 6

- Using a diagram describe the working of box of a solar cooker.. State two disadvantages

- Explain the following terminologies as used by solar cells

- Short circuit current (Isc)

- Open circuit voltage (Voc)

- Explain how solar cell works

Tests procedures for an installation

- Physical inspection

- Electrical tests

- Ring continuity tests

- Effectiveness of the earth tests

- Insulation tests

- Polarity tests

Electrical regulations governing solar installations

TEST 2

- A. state two

- Forms of energy conversion which are derived form the sun

- Applications for each type of energy in (i) above			(4mks)

- With aid of diagram, distinguish between diffuse and direct solar radiation